APPLICATION:	WATERPROOFING

ASSEMBLY:		STANDARD

180 MILS

MONOLITHIC MEMBRANE 6125®

LONG FORM SPECIFICATION

PART I GENERAL

1.01	SUMMARY

A.	This specification serves as a guideline and should be adapted to suit the needs of each individual project by the architect.  It is prepared in accordance with the CSI three-part section format and should be included as a separate section under DIVISION 7 - Thermal and Moisture Protection. Improvements and other changes to the contents may be made only with the written approval of the architect.

1.02	RELATED SECTIONS (Note to Specifier: Edit to project requirements)

A.	DIVISION 2 - Sitework [Section 02500/02870] - Paving/Site Furnishings as supplied by American Hydrotech, Inc.  See Division 7 for specific details.

B.	DIVISION 3 - Concrete [Section 03300] - Roof Deck Surface/Substrate

The coordination of this section is necessary to facilitate the successful installation of the waterproofing membrane.

Cast in Place Concrete/Composite Deck

1.	Strength/density:	minimum  2,500 psi (17,235 kPa) compressive strength

minimum 115 pcf (1842 kg/m3) density

2.	Finish:			Broom finish or equivalent similar to ICRI CSP 3 to 5.  Steel

troweled finish is not desirable.

3.	Concrete Hydration (Cure):

a.	Method of Cure:  Water cure, wet coverings, paper sheets, plastic sheets or approved liquid curing compound (sodium silicate preferred).

b.	Duration of Cure/Dry:

i.	Structural Weight Concrete:  recommend 28 days, minimum 14 days, prior to application of the membrane.

ii.	Lightweight Structural Concrete:  recommend 60 days, minimum 28 days, prior to application of membrane. Venting of the deck from the underside is recommended to facilitate drying.

iii.	The above minimum cure/dry times are recommended based upon basic concrete fundamentals and experience. Depending on conditions (i.e., ambient temperature, humidity) the concrete may be dry enough to receive application of the membrane in less than the 14 day minimum recommendation. Consult Hydrotech for specifics when less than the minimum is desired.

- Form Release Agents: Contact Hydrotech

*REFER TO SECTION 3.02 PREPARATION, FOR ADDITIONAL SUBSTRATE TYPES*

C.	DIVISION  [ ] - Wood blocking and curbing

D.	DIVISION  [ ] - Insulation

E.	DIVISION  [ ] - Sheet metal flashing and counterflashing

F.	DIVISION  [ ] - Caulking and sealants

G.	DIVISION  [ ] - Plumbing specialties

1.03	REFERENCES

A.	American Society for Testing and Materials (ASTM).

B.	Canadian General Standards Board CGSB-37.50-M89, Standard for "Asphalt, Rubberized, Hot Applied, for Roofing and Waterproofing."

C.	International Concrete Repair Institute (ICRI) Concrete Surface Profile (CSP) Scale.

1.04	SYSTEM DESCRIPTION

A.	Furnish and install a completed vertical or horizontal waterproofing assembly including surface conditioner, Monolithic Membrane 6125®-FR and related flashings, protection course, Styrofoam™ brand insulation (if required), drainage course (if required), and pavers (if required).

1.05	SUBMITTALS

A.	Certification from an approved independent testing laboratory experienced in testing this type material, that the material meets the CGSB-37.50-M89 standard for rubberized asphalt membranes, including applicable ASTM procedures.

- Certification that the roofing membrane has current validation by Underwriters Laboratories, or other approved independent validation service provider, of a minimum 40% recycled content (post-consumer).

C.	Certification showing full time quality control of production facilities responsible for the manufacture of the rubberized asphalt and that each batch of material is tested to insure conformance with the manufacturers published physical properties.

- Certification that the plant manufacturing this material has IS0 9001-2015 approval as evidenced by a copy of the official certificate.

E.	Certification showing that all roofing components are being supplied and warranted by a single-source manufacturer.

- Certification that the extruded polystyrene insulation if used is free from CFC's.

1.06	QUALITY ASSURANCE

A.	The Waterproofing Contractor shall demonstrate qualifications to perform the work of this Section by submitting the following documentation:

1.	Certification or license by the membrane manufacturer as a locally based, authorized applicator of the product the installer intends to use, for a minimum of five (5) years.

2.	List of at least three (3) projects, satisfactorily completed within the past five (5) years, of similar scope and complexity to this project.  Previous experience submittal shall correspond to specific membrane system proposed for use by applicator.

B.	Refer to Section 1.04 SYSTEM DESCRIPTION.  Include single-source for all components from the manufacturer.

C.	The rubberized asphalt membrane product shall contain an inert filler and crumb rubber to enable the product to be resistant to acids (fertilizers, building washes and acid rain) and maintain membrane thickness during application respectively.

D.	Membrane Manufacturer shall have available an in-house technical staff to assist the contractor, when necessary, in application of the products and final inspection of the assembly.

E.	Membrane Manufacturer Qualification:  Manufacturer shall demonstrate qualifications to supply materials of this section by certifying the following:

1.	Membrane Manufacturer must show evidence that the specified rubberized asphalt has been manufactured by the same source for thirty five (35) years and successfully installed on a yearly basis for a minimum of thirty five (35) years on projects of similar scope and complexity.

2.	Membrane Manufacturer must not issue warranties for terms longer than they have been manufacturing their hot fluid rubberized asphalt membrane.

F.	Pre-Construction Conferences.  The manufacturer will meet with the necessary parties at the jobsite to review and discuss project conditions as it relates to the integrity of the waterproofing assembly.

1.07	DELIVERY, STORAGE AND HANDLING

A.	Deliver materials in original unopened containers of packaging clearly labeled with manufacturer's name, brand name, instruction for use and all identifying numbers.

B.	Materials shall be stored in a neat, safe manner, not to exceed the allowable structural capacity of the storage area.

C.	Store materials in a clean, dry area protected from water and direct sunlight.

- Store all adhesives at temperatures between 60°F (15.5°C) and 80°F (26.6°C).  If exposed to lower temperatures, restore materials to 60°F (15.5°C) minimum temperature before using.

1.08	PROJECT CONDITIONS

A.	Application of the membrane shall not commence nor proceed during inclement weather.  All surfaces to receive the membrane shall be free of water, dew, frost, snow and ice.

B.	Application of membrane shall not commence nor proceed when the ambient temperature is below 0°F (-17.7°C).

C.	Preparation and application of membrane must be conducted in well ventilated areas.

D.	Over its service life, do not expose membrane or accessories to a constant temperature in excess of 180°F (82°C) (i.e., hot pipes and vents or direct steam venting, etc.).

E.	Adhesives contain petroleum distillates and are extremely flammable.  Do not breathe vapors or use near an open fire.  Do not use in confined areas without adequate ventilation.  Consult container or packaging labels and Material Safety Data Sheets (MSDS) for specific safety information.

F.	Do not allow waste products (petroleum, grease, oil, solvents, vegetable or mineral oil, animal fat, etc.) to come in contact with the roof membrane.  Any exposure to foreign materials or chemical discharges must be presented to membrane manufacturer for evaluation to determine any impact on the waterproof membrane assembly performance.

G.	Concrete Deck/Wall Surface Condition.  IMPORTANT - Refer to 1.02 Related Sections.

H.	Deck/Wall Preparation; refer to Section 3.02 Preparation.

- The project design professional shall design the roofing/waterproofing assembly to properly locate the dew point condition and determine the need and location for a vapor retarder to prevent excessive condensation contamination within the roofing/waterproofing assembly and/or delamination of the roofing/waterproofing membrane from the substrate.

- General contractor shall assure that adequate protection is provided after installation of the membrane and accessories to prevent damage from subsequent trade traffic.

1.09	WARRANTY

A.	Upon completion of the work, the contractor must supply the owner with a single-source warranty of U.S. origin direct from the manufacturer.

B.	Each warranty varies in scope and terms.  CONTACT Hydrotech for exact warranty terms and conditions to meet the specific project requirements.

C.	Warranties available from the manufacturer: (Note to Specifier: Edit to project requirements)

1.	Material Warranties; excludes labor.

Duration:  5-, 10-, 15-, 20-year

2.	Watertightness Warranties; includes labor and material to maintain watertight condition.

Duration:  5-years

3.	Thermal Warranties; includes 90% retention of the original thermal value.

Duration 5-, 10-, 15-years

4.	Total System Warranties; covers components of the waterproofing assembly, including membrane, flashing, insulation and pavers.  Includes removal and reinstallation of the insulation and pedestal installed pavers when installed per Hydrotech's requirements.

  - Duration of Membrane/Flashing from date of installation: 5-year (watertight condition)

  - Duration of Insulation from date of purchase:  5-, 10-, 15-year (90% of original thermal value)

  - Duration of Pavers from date of purchase: 5-, 10-year (will not crack, split or delaminate due to freeze-thaw)

**CONTACT HYDROTECH FOR EXACT WARRANTY TERMS AND CONDITIONS.**

PART II PRODUCTS

2.01	GENERAL

A.	Refer to Section 1.04, SYSTEM DESCRIPTION.  All components must be obtained as a single-source from the membrane manufacturer to ensure total system compatibility and integrity.

Manufacturer:		American Hydrotech, Inc.

401 N. Michigan Ave, Suite 1550

Chicago, Illinois 60611

800-877-6125 or 312-337-4998

Web Site:  www.hydrotechusa.com

2.02	MATERIALS

A.	Membrane

1.	Membrane shall be a hot, fluid applied, rubberized asphalt membrane meeting the following CGSB-37.50-M89 standard and other pertinent physical properties: (Note to Specifier: Edit to project requirements)

- American Hydrotech, Inc., Monolithic Membrane 6125®

(40% post-consumer recycled content)

| PROPERTY | TEST METHOD | - REQUIREMENT |
| --- | --- | --- |
| Flash point | CGSB-37.50-M89 ASTM D-92 | > 500°F* (260°C) |
| Penetration | CGSB-37.50-M89 ASTM D-5329 | @ 77°F (25°C) max. 110 @ 122°F (50°C) max. 200 |
| Flow | CGSB-37.50-M89 ASTM D-5329 | @ 140°F (60°C) max. 3.0mm |
| Toughness | CGSB-37.50-M89 | ≥ 5.5 Joules |
| Ratio of Toughness to Peak Load | CGSB-37.50-M89 | ≥ 0.040 |
| Water Vapor Permeability | CGSB-37.50-M89 ASTM E-96, Procedure E | ≤ 1.7 ng/Pa.s.m2 (0.027 perm) |
| Water Absorption | CGSB-37.50-M89 | Gain in weight 0.35 g max. Loss in weight 0.18 g max. |
| Low Temperature Flexibility (-25°C) | CGSB-37.50-M89 | No delamination, adhesion loss, or cracking |
| Low Temperature Crack Bridging Capability | CGSB-37.50-M89 | No cracking, adhesion loss, or splitting |
| Heat Stability | CGSB-37.50-M89 | No change in viscosity, penetration, flow or low temperature flexibility |
| Viscosity | CGSB-37.50-M89 | 2 - 15 seconds |
| Water Resistance (5 days/50°C) | CGSB-37.50-M89 | No delamination, blistering, emulsification, or deterioration |
| Softening Point | ASTM D-36 | 180°F (82°C) |
| Elongation | ASTM D-5329 | 1000% minimum |
| Resiliency | ASTM D-5329 | 40% minimum |
| Bond to Concrete 0°F (-18°C) | ASTM D-5329 | Pass |
| Resistance to Acid | ASTM D-896 Procedure 7.1 (N-8) | Pass - 50% Nitric Acid Pass - 50% Sulfuric Acid |
| Resistance to Hydrostatic Pressure | ASTM D-08.22 Draft 2 | 100 psi (equals 231 foot of head water) |
| Resistance to Salt Water (20% Sodium carbonate calcium chloride) | ASTM D-896 similar | No delamination, blistering, emulsification or deterioration |
| Resistance to Fertilizer (Undiluted 15/5/5, nitrogen/phosphorus/potash) | ASTM D-896 similar | No delamination, blistering, emulsification or deterioration |
| Resistance to Animal Waste | 3-year exposure | No deterioration |
| Solids Content |  | 100% - no solvents |
| Recycled Content | UL Validated | 40% (post-consumer) (30% REACH compliant) |
| Shelf Life |  | 10 years (sealed) |
| Specific Gravity |  | 1.15 + .02 |
| * Or alternatively not less than 25oC above the manufacturer’s maximum recommended application temperature |  |  |

B.	Surface Conditioner

1.	Asphaltic surface conditioner for concrete surfaces.

- American Hydrotech, Inc., Surface Conditioner

C.	Flashing/Reinforcing (Note to Specifier: Edit to project requirements)

1.	60-mil (1.5 mm) thick, uncured neoprene flashing/(heavy duty) reinforcing sheet.

- American Hydrotech, Inc., Flex Flash UN®

2.	Spunbonded polyester fabric reinforcing sheet.

- American Hydrotech, Inc., Flex Flash F®

- Two-component, liquid applied resin membrane flashing system.

- American Hydrotech, Inc., HydroSeal Resin

- poly methyl-methacrylate (PMMA) resin

- American Hydrotech, Inc., HydroSeal Matrix

- acrylic resin with integral chopped polymer fiber reinforcement

- American Hydrotech, Inc., HydroSeal Flashing Accessories

- resin based primers, additives, reinforcing fleece, surfacing topcoats

4. 	One-component, liquid applied membrane flashing system

- American Hydrotech, Inc., HydroSeal 1K PU – Membrane

- Aliphatic and alkaline resistant, low VOC polyurethane (PU) resin

- American Hydrotech, Inc., HydroSeal 1K accessories

- Epoxy based primer, fiber reinforcement, fleece

(Note to Specifier: CONSULT Hydrotech for recommended products

and uses.)

D.	Adhesives/Sealant (Note to Specifier: Edit to project requirements)

1.	Contact adhesive to bond elastomeric flashing together.

- American Hydrotech, Inc., Splicing Cement

2.	Pressure sensitive butyl tape to bond elastomeric flashing together.

- American Hydrotech, Inc., Splice Tape

3.	Contact adhesive to bond elastomeric flashing to an approved substrate.

- American Hydrotech, Inc., Bonding Adhesive

4.	Sealant to seal elastomeric flashing seam edge.

- American Hydrotech, Inc., Lap Sealant

E.	Protection Course (Note to Specifier: Edit to project requirements)

1.	Fiberglass reinforced rubberized asphalt sheet.

- American Hydrotech, Inc., Hydroflex® 30

- Extruded polystyrene, rigid, insulating, drainage board (vertical applications only)

- American Hydrotech, Inc., Thermaflo™

- Extruded polystyrene, rigid, insulation board (vertical applications only)

- Styrofoam™ brand insulation as manufactured by DuPont™, marketed by American Hydrotech, Inc., Protection Board, SM, RM

**Certain project conditions may warrant additional protection. CONTACT Hydrotech**

F.	Prefabricated Drainage Course (if required) (Note to Specifier: Edit to project requirements)

1.	Composite drainage system consisting of a three-dimensional, crush-proof, drainage core and a filter fabric meeting the following physical properties.

- American Hydrotech, Inc., Hydrodrain® 300, 400, 700 or 1000 series

| PROPERTY | TEST METHOD | ## VALUES |
| --- | --- | --- |
| CORE: |  |  |
| Compressive Strength | ASTM D-1621 | 300/302/1000 - 30,000 psf (14.66 kg/cm2) 400/420 - 15,000 psf (7.32 kg/cm2) 700 - 18,000 psf (8.79 kg/cm2) |
| Thickness | ASTM D-1777 | 1000 - .25 in (.64 cm) 300/302 - .22 in (.56 cm) 400/420/700 - .40 in (1.016 cm) |
| Flow, Q @ 3600 psf & hydraulic gradient of 1 | ASTM D-4716 | 300/1000 - 7 gpm/ft width (72.00 lpmin/m width) 302 - 5.5 gpm/ft width (68.30 lpmin/m width) 400/420 - 15 gpm/ft width (183.3 lpmin/m width) 700 - 18 gpm/ft width (223.52 lpmin/m width) |
| FABRIC: |  |  |
| Flow | ASTM D-4491 | 300/302/1000 - 150 gpm/ft2 (6105 lpmin/m2) 400/420 - 150 gpm/ft2 (6105 lpmin/m2) 700 - 110 gpm/ft2 (4475 lpmin/ft2) |
| U.V. Resistance | ASTM D-4355 | Fully Stabilized |
| Apparent Opening Size (EOS) | CW-02215 | 300/302/400/420/1000 – 70 (.212mm) 700 – 30 (.60 mm) |
| Grab Tensile | ASTM D-4632 | 300/302/400/420/1000 - 90 lbs. (0.4 kN) 700 – 360x260 lbs. (445x355 N) |

- Extruded polystyrene, rigid, insulating, drainage board (vertical applications only)

- American Hydrotech, Inc., Thermaflo™

G.	Insulation (Note to Specifier: Edit to project requirements)

1.	Extruded polystyrene rigid board insulation meeting the following physical properties.

- Styrofoam™ Brand insulation [TYPE] as manufactured by DuPont™, marketed by American Hydrotech, Inc.

a.	Insulation shall meet ASTM C-578, Type VI or VII.

b.	Minimum compressive strength, ASTM D-1621, 40 or 60 psi (276 or 414 kPa) (variance by type of product)

c.	Maximum water absorption by volume per ASTM C-272, 0.3%

d.	Water vapor permeance for 1" product per ASTM E-96, 0.8 perm (max.) (63 ng/Pa/s/m2).

e.	Insulation shall have an R value of 5.0 F ft2 h/Btu/in. (0.88 K m2/W) of thickness when tested at 75°F (23.9°C) mean temperature in accordance with ASTM C-518

f.	Product shall be free of CFC's

Product types available: Styrofoam™ Brand Plaza Deck; High Load 100; and Square Edge. (Note to Specifier: CONSULT Hydrotech for recommended product type.)

H.	Filter Fabric (if required)

1.	Water permeable polymeric fabric.

- American Hydrotech, Inc., Stone Filter Fabric

I.	Topping Materials (Note to Specifier: Edit to project requirements)

1.	Pavers

a.	Architectural Finish Pavers

-American Hydrotech, Inc., Architectural Pavers, meeting the following physical properties:

| PROPERTY | TEST METHOD | VALUES |
| --- | --- | --- |
| Compressive Strength | ASTM C140 | >8,500 psi average min. |
| Flexural Strength | ASTM C293 | >1,100 psi average min. |
| Water Absorption | ASTM C140 | Not greater than 5% |
| Freeze/Thaw | ASTM C67 | <1% loss/dry weight (50 Cycles) |
| Centerload | - | Min. 1,750 lbs. |

b.	Paver Accessories

- Fixed Height pedestals as recommended by American Hydrotech, Inc.

- Adjustable Height pedestals as recommended by American Hydrotech, Inc.

- Concrete Pour Topping

(Note to specifier: DuPont™, manufacturers of Styrofoam™

brand insulation, recommends the incorporation of an air layer between the

insulation and concrete.  Hydrotech suggests the use of Hydrodrain® AL for this

purpose.)

3.	Asphalt Paving Overlay

(Note to specifier: When asphalt paving will be placed directly over the

waterproofing, CONTACT Hydrotech for suggestions and recommendations.)

- Miscellaneous

1. 	Prefabricated Concrete Curbing

High density, hydraulically pressed, prefabricated concrete curbing units as shown on plans and details.

- 	Hanover Architectural Products Rock Curb® as marketed by American Hydrotech, Inc. size as noted on plans and details. (Note to Specifier:  Per standard product line:  please indicate configuration, layout, size, color and edge profile of Rock Curb® on plans and details)

PART III EXECUTION

3.01	INSPECTION

A.	The waterproofing contractor shall examine all surfaces to receive the waterproofing assembly to verify it is acceptable and proper for the application of the membrane.  Refer to American Hydrotech's Pre-Installation & Application Guidelines.

B.	The waterproofing contractor shall not proceed with the installation of the waterproof membrane assembly until all deck defects have been corrected.

3.02	PREPARATION

A.	All surfaces must be dry, smooth, free of depressions, voids, protrusions, clean and free of unapproved curing compounds, form release agents and other surface contaminants.

(Note to Specifier: Edit ot project requirements)

1.	Cast in-place concrete/Composite deck

a.	Poured in place concrete must be monolithic, smooth, free of voids, spalled areas, laitance, honeycombs, and sharp protrusions.

b.	Refer to Section 1.02 of this specification, Division 3.

2.	Precast concrete decks

a.	Precast units shall be mechanically secured to minimize differential movement and all joints between units shall be grouted or caulked.

b.	Joints shall be pre-detailed with membrane and the appropriate manufacturer required reinforcing prior to full membrane application.

3.	Retrofit/Tear-Off Application**

**REFER TO MM6125 WATERPROOFING FABRIC-REINFORCED SPECIFICATION**

B.	Substrate cleaning

1.	Thoroughly sweep the substrate which is to receive the waterproofing membrane.

2.	Substrate must also be blown clean using an air compressor to remove any remaining loose debris.

3.	Final check to determine if concrete has been properly cleaned is to apply a test patch of Monolithic Membrane 6125 to the surface and check its adhesion.

3.03	INSTALLATION

A.	Surface conditioner application (to concrete)

1.	Apply the surface conditioner to the concrete using a hand held sprayer evenly at a rate of 300 to 600 SF/gallon (7.4 - 14.7 m2/L) depending on surface texture.  Surface conditioner should "tan" the surface, not blacken it.

2.	Allow sufficient time for the surface conditioner to thoroughly dry prior to the membrane application.

B.	Membrane preparation

1.	The membrane shall be heated in double jacketed, oil bath or hot air melter with mechanical agitation, specifically designed for the preparation of a rubberized asphalt membrane.

2.	Heat membrane until membrane can be drawn-free flowing at a temperature range between 350°F (176°C) and 375°F (190°C).

C.	Detailing/Flashing

1.	All detailing and flashing shall be done in accordance with the manufacturer's standard guideline details.

2.	All detailing and flashing shall be completed before installing the membrane over the field of the substrate.

- All liquid-applied, resin flashings shall be applied over properly completed membrane flashing details in accordance with the manufacturer’s standard guideline details.

D.	Membrane Application

1.	Apply the rubberized asphalt membrane at a rate to provide a continuous, monolithic coat of 180 mil minimum (approximately 3/15", 4.6 mm), but not less than 125 mil (1/8", 3.2 mm) thickness.

3.04	SEPARATION/PROTECTION LAYER INSTALLATION

- Protection layer shall be installed as follows:

1.	Embed the protection sheet/rigid insulation board into the membrane while it is still warm to insure a good bond.

2.	Overlap adjoining sheet edges (dry) a minimum of 2"-3" (50.8 mm - 76.2 mm) to insure complete coverage. Rigid insulation board materials are not to be overlapped.

3.	The completed membrane/protection assembly must be covered with subsequent topping materials as soon as possible, within 30 days of membrane installation.

3.05	MEMBRANE INTEGRITY TEST

- The roof area or portions thereof shall be leak tested by means of Electronic Leak Detection (ELD) or by ponding water at a minimum depth of 2" (50.8 mm) for a period of 48 hours to check the integrity of the membrane installation.

  - ELD testing should be performed on all installed membrane assembly. Testing is to be performed in accordance with ASTM D7877 or ASTM D8231. Areas that are ELD tested should be covered immediately

  - VERIFY that the structure can support the deadload weight of a water test before testing.

  - If leaks should occur the water shall be drained completely and the membrane installation repaired.

- In the event of excessive damage to the membrane assembly, Electronic Leak Detection testing shall be required prior to the placement of subsequent overburden.

3.06	DRAINAGE COURSE / INSULATION / FILTER FABRIC /PAVER PLACEMENT

A.	General

1.	Examine the deck area to be covered with subsequent topping materials in order to insure that all deck areas have received the membrane, the membrane is free of damage, it is properly protected, and all flashing has been properly installed, before placing the insulation.

2.	It is recommended that the drainage course (if required), insulation (if required), and other subsequent topping materials be installed as each section is completed.

B.	Prefabricated Drainage Course Placement (if required)

1.	Install drainage course on horizontal and vertical surfaces in accordance with the manufacturer's recommendations.

2.	Layout and position drainage course and allow to lay flat.  Cut and fit drainage course to perimeter and penetrations.

3.	The geotextile overlapped edges may be bonded to the adjacent drainage course geotextile with an appropriate adhesive to ensure continuous geotextile integrity.

4.	Drainage course shall be covered with subsequent overburden within 10 – 14 days of installation.

(Note to specifier: If drainage layer is being installed as an AIR LAYER, placement of the drainage course follows installation of insulation (if required). CONTACT Hydrotech.)

C.	Insulation Placement (if required)

1.	Loose lay horizontal applications) in a staggered manner and tightly butt together all insulation boards.  The maximum acceptable opening between insulation boards is 3/8" (9.5 mm).  Insulation must be installed within 3/4" (19 mm) of all projections, penetrations, etc.

- When multi-layer insulation applications are involved the bottom layer of insulation must be the thickest layer and must be a minimum of 2" thick (50.8 mm).  All layers shall be installed unadhered to each other and all joints staggered in relation to underlying layers.

- For vertical, multi-layer applications, second layer of insulation board may be spot adhered to the protection layer with appropriate adhesive or additional rubberized asphalt membrane.

D.	Architectural Finish Paver Placement (if required)

1.	Install architectural finish pavers on tabs or pedestals in accordance with manufacturer's recommendations and architectural layout.

(Note to specifier: Fabric is not required under full paver installations, however, may be desirable to mask insulation color at joints between pavers.)

- Black, fabric-covered insulation shall not be left exposed in ambient temperatures greater than or equal to 90°F. Measures to maintain temperatures at insulation surface below 165°F shall be implemented.

3.07	JOB COMPLETION

A.	Contractor and a representative of the membrane manufacturer shall inspect the waterproofing assembly and notify the contractor of any defects.  All defects must be corrected.

B.	Clean up all debris and equipment.

END OF SECTION